AMITY REGIONAL SCHOOL DISTRICT #5

PREVENTIVE MAINTENANCE

## PROCEDURE MANUAL

TABLE OF CONTENTS

INTRODUCTION – PREVENTIVE MAINTENANCE	1

1.  SITE INPSECTION PROCEDURE	2

2.  BUILDING INSPECTION PROCEDURE	3

3.  ROOF INSPECTION PROCEDURE	4

4.  HVAC INSPECTION PROCEDURE	5

5.  CLASSROOM AND COMMON AREA INSPECTION PROCEDURE	7

APPENDIX	9

INTRODUCTION – PREVENTIVE MAINTENANCE

This handbook details the Preventive Maintenance Procedures utilized by the Amity Regional  School’s Facilities Department.  Preventive Maintenance is a proactive program designed to ensure the on-going operations of the District facilities with a minimal impact to the student population due to unforeseen equipment failures.  Preventive Maintenance will help improve equipment reliability, help avoid any unplanned maintenance activity, reduce energy use, and increase the life of capital equipment.  This program will aid Amity Regional Schools in conforming to OSHA, EPA, and State of Connecticut regulations.

This manual is divided into specific chapters with specific procedures for building, site, roof, classroom/common area, and HVAC equipment inspections.  Copies of all inspection formats are included in the appendix.

Preventive maintenance on fire alarm systems, kitchen hoods, suppression systems, sewage discharge pumps, well pumps, and sprinkler systems require licensed or certified personnel and thus are contracted on an annual basis.  The record-keeping for these items can be found in the Facilities Office.

1.  SITE INSPECTION PROCEDURE

- All District sites will be inspected annually.

- During the inspection staff shall note findings on the Site Inspection Report form.  Minor deficiencies shall be repaired during the course of inspection.  Other areas needing attention shall be recorded and forwarded to the Facilities Director for action.

- PARKING/BUS AREA – Physically inspect the parking lot and drive surfaces. Note any potholes and overall condition.

- SIDEWALKS – Physically inspect sidewalks.  Pay particular attention to “heaved” and uneven areas.  Mark heaved areas with traffic paint until repaired.

- HARD SURFACE COURTS – Physically inspect all play areas and outdoor seating.   Note overall condition.

- SITE LIGHTING – Physically inspect all outdoor area light fixtures/poles.  Energize lights and check lamps for proper operation.  Set time clocks if applicable.

- FENCING – Physically inspect fencing.  Check gates for proper operation and security.

- TREES - Visually inspect all trees.  Check for root damage to surrounding area, hanging branches, noticeably cracked branches, apparent diseased or dying areas.

- PLAYGROUNDS – Physically inspect playground area and equipment.  Check for broken and missing equipment components.  Check the condition of the ground-cushioning agent.  Assess the overall condition of the playground.  Report any safety concerns to the Facilities Director immediately. NOTE Playgrounds shall be inspected monthly to ensure safe conditions are maintained.

2.  BUILDING INSPECTION PROCEDURE

- All District buildings at all sites will be inspected annually.

- During the inspection staff shall note findings on the Building Inspection Report form.  Minor deficiencies shall be repaired during the course of inspection.  Other areas needing attention shall be recorded and forwarded to the Facilities Director for action.

- EXTERIOR WALLS – Physically inspect the wall condition for cracks, dryrot, paint deficiencies, and graffiti.  Any crack or deterioration that may severely affect the integrity of the structure shall be brought to the immediate attention of the Facilities Director.

- FOUNDATION – Physically inspect the visible exterior foundation.  Particular attention shall be paid to cracks and/or separation at the foundation line.

- EXTERIOR DOORS/HARDWARE – Physically inspect all building entry doors.  Inspect the door for overall condition and security.  Tighten and lubricate hinges as necessary.  Inspect the closer for leaks and mounting.  Verify the closer is damping properly and adjust if needed.  Inspect panic hardware and locksets.

- WINDOW /WALL SYSTEMS – Physically inspect the window systems for integrity.  Note any cracked and broken glazing, assess the condition of glazing putty, if applicable, and assess the general condition and operation of the window system.  Inspect condition of window wall solid wall panels.

- ROOFS – Refer to Roof Inspection Procedures.

3.  ROOF INSPECTION PROCEDURE

- All District roofs will be inspected bi-annually.

- Inspect all roofs prior to the beginning of the winter season, beginning inspections during September, with all inspections completed no later than October 31.

- Inspect all roofs prior to the beginning of the summer season, beginning inspections during April, with all inspections completed no later than May 31.

- During the inspection staff shall note findings on the Roof Inspection Report form.  Minor deficiencies shall be repaired during the course of inspection.  Other areas needing attention shall be recorded and forwarded to the Facilities Director for action.

- ROOFS - Physically inspect all roof surfaces for excessive wear, blistered areas, areas of standing water, or separations of the roofing materials.  Inspect and seal flashings.

- EAVES/SOFFITS – Physically inspect all eave and soffit overhangs for dryrot, sagging, and paint deficiencies.

- GUTTERS - Physically inspect all gutters, downspouts, and roof scuppers/drains for a free and unrestricted flow.  Report and repair any deficient components.  Clear obstructions and remove debris.

- LEAKS  - If a leak has been reported and the source is not readily apparent, run water across the roof surface to determine the source.  Make repairs as needed.  If substantial roof repairs are needed make temporary repairs, as necessary, and notify the Facilities Director.

7.    TASKS – Regularly remove debris from roofs and clear all roof drains.

4.  HVAC INSPECTION PROCEDURE

- All District HVAC Systems will be inspected at intervals utilizing the SchoolDude Preventive Maintenance Module.  In addition:

- Inspect all cooling units prior to the beginning of the summer season, beginning inspections during March, with all inspections completed no later than April 30.

- Inspect all heating units prior to the beginning of the winter season, beginning inspections during September, with all inspections completed no later than October 31.

- During the inspection staff shall note findings on the HVAC Inspection Report form and on the Preventive Maintenance work order generated on the SchoolDude work order system.  Minor deficiencies shall be repaired during the course of inspection.  Other areas needing attention shall be recorded and forwarded to the Facilities Director for action.

- AIR CONDITIONING UNITS / CHILLERS –

- Physically inspect and clean all coils (evaporator and condenser), inspect and lubricate motors and shafts (if applicable), inspect fan belts (if applicable), inspect plenums/duct connections, inspect and change air filters, inspect major electrical connections, inspect air handling units, inspect condition of condensate drain and drain pan, assess overall condition of unit.

- Energize unit and check general operation.  Record operating pressures.  Record supply and return temperatures.  Check for proper airflow at registers. Verify motor current draw is within manufacturer’s specifications.  Check thermostats for proper operation.

- EVAPORATIVE COOLERS / COOLING TOWERS –

- Physically inspect unit and related piping for leaks, drain and clean unit, inspect/replace pads (if applicable), inspect and lubricate motors and shafts (if applicable), inspect fan belts (if applicable), inspect major electrical connections, inspect pumps, assess overall condition of unit.

- Energize unit and check general operation.  Verify motor current draw is within manufacturer’s specifications. Check controls for proper operation.

- HEATING UNITS / BOILERS -

- Physically inspect surrounding area for housekeeping (no flammable storage, etc), inspect and clean gas/oil valve and burner assembly (if applicable), leak check all gas/oil piping, inspect flue for proper installation, inspect and lubricate motors, shafts and pumps (if applicable), inspect fan belts (if applicable), inspect air handling units, inspect plenums/duct connections, inspect and change air filters, inspect major electrical connections, inspect safety devices (relief valves, hi-limits, etc), assess overall condition of unit.  Inspect air compressors and change oil as needed.  Inspect all pipe and boiler insulation for damage and note under “other”.

- Energize unit and check general operation.  Record supply and return temperatures.  Check for proper airflow at registers. Verify motor current draw is within manufacturer’s specifications.  Check thermostats for proper operation.

- Inspect unit ventilators in classrooms.  Clean or replace filters.  Clean unit with vacuum cleaner.  Lubricate motors, shafts and pumps as necessary.  Verify damper and thermostat operation.

5.  CLASSROOM AND COMMON AREA INSPECTION PROCEDURE

- All District classrooms and common areas at all sites will be inspected annually.

- During the inspection staff shall note findings on the Classroom Inspection Report form or the Common Area/Restroom Inspection Report form.  Minor deficiencies shall be repaired during the course of inspection.  Other areas needing attention shall be recorded and forwarded to the Facilities Director for action.

- ENTRANCE – Physically inspect the entrance area.  Check ramp and handrails, if applicable.  Inspect the door for overall condition and security.  Tighten and lubricate hinges as necessary.  Inspect the closer for leaks and mounting.  Verify the closer is damping properly and adjust if needed.  Inspect lockset.

- FLOOR COVERING – Physically inspect all floor areas.  Check for loose/worn carpet and/or floor tile.  On raised foundation wood sub-floors, inspect for dryrot, especially at entry threshold area.  If asbestos tile is damaged, alert LEA Designated Person (Facilities Director) immediately.

- WALLS – Physically inspect all interior wall surfaces.  Check for loose or missing wall base.  Inspect for holes or graffiti.  Note condition of wall coverings and paint.

- WINDOWS – Physically inspect all windows for proper operation and security.  Check all hardware.

- CEILINGS – Physically inspect ceiling area.  Investigate all water-stained areas.  For suspended ceilings, ensure tiles are properly installed.  Replace damaged/missing tiles.

- ELECTRICAL – Physically inspect all light fixtures, switches and outlets.  Ensure cover plates are in place and secure.  Check/tighten electrical connections at breaker panels.

- INTERCOM – Verify operation of intercom.

- PLUMBING – Physically inspect all plumbing fixtures and connections.  Check all risers, stops, and traps for leaks.  Rebuild faucets as needed.  Repair/replace any leaking fixtures.  Verify drains flow freely.

- CABINETS/COUNTERTOPS – Physically inspect all cabinets and countertops.  Inspect all cabinet hardware.  Note any major damage to countertops.

- HVAC– Physically inspect the visible components in the classroom.  Verify the registers/grills are in place and open.  Inspect the thermostat. Assess the operation of the HVAC system.

- EXHAUST FANS – Remove, clean, and lubricate exhaust fan assemblies.

APPENDIX

SITE INSPECTION FORM	I

BUILDING INSPECTION FORM 	II

ROOF INSPECTION REPORT 	III

HVAC INSPECTION FORM	IV

CLASSROOM INSPECTION FORM	V

COMMON AREA/RESTROOM INSPECTION 	VI

AMITY REGIONAL SCHOOLS

PREVENTIVE MAINTENANCE – SITE INSPECTION FORM

| Site Name: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Site Address: |  |  |  |  |
| Area/Item Inspected: | Condition (check one) | Comments: |  |  |
| Parking/Bus Area | Good Fair Poor |  |  |  |
| Sidewalks | Good Fair Poor |  |  |  |
| Hard-surface Courts | Good Fair Poor |  |  |  |
| Site Lighting | Good Fair Poor |  |  |  |
| Fencing | Good Fair Poor |  |  |  |
| Trees | Good Fair Poor |  |  |  |
| Playground 1(indicate location)) | Good Fair Poor |  |  |  |
| Playground 2 (indicate location) | Good Fair Poor |  |  |  |
| Playground 3 (indicate location) | Good Fair Poor |  |  |  |
| OVERALL CONDITION OF SITE (check box) Good Fair Poor General Remarks: |  |  |  |  |
| Repairs Needed |  |  | WO Number: | Repaired By: |
| Inspected by (print name): |  |  | Date: |  |

AMITY REGIONAL SCHOOLS

PREVENTIVE MAINTENANCE – BUILDING INSPECTION FORM

| Site Name: |  |  |
| --- | --- | --- |
| Site Address: |  |  |
| Building / Wing Number: |  |  |
| Building Construction Type (brick, wood, portable, etc) |  |  |
| Building Construction Date (if known) |  |  |
| North Wall (check box) Good Fair Poor Comments: |  |  |
| West Wall (check box) Good Fair Poor Comments: |  |  |
| South Wall (check box) Good Fair Poor Comments: |  |  |
| East Wall (check box) Good Fair Poor Comments: |  |  |
| Window Systems (check box) Good Fair Poor Comments: |  |  |
| Entry Doors/Hardware (check box) Good Fair Poor Comments: |  |  |
| OVERALL CONDITION OF BUILDING (check box) Good Fair Poor General Remarks: |  |  |
| Repairs Needed | WO Number: | Repaired By: |
| Inspected by (print name): | Date: |  |

AMITY REGIONAL SCHOOLS

PREVENTIVE MAINTENANCE - ROOF INSPECTION REPORT

| Site Name: |  |  |  |
| --- | --- | --- | --- |
| Site Address: |  |  |  |
| Building / Wing Number: |  |  |  |
| Roof Type (metal, foam, etc) | Pitch: |  |  |
| Roof Age (if known) |  |  |  |
| Roof Surface Condition (check box) Good Fair Poor Comments: |  |  |  |
| Equipment Flashings (check box) Good Fair Poor Comments: |  |  |  |
| Roof to Wall Connections (check box) Good Fair Poor Comments: |  |  |  |
| Roof Gutters and Drains (check box) Clean and unobstructed Needs Repair Comments: |  |  |  |
| OVERALL CONDITION OF ROOF SYSTEM (check box) Good Fair Poor General Remarks: |  |  |  |
| Repairs Needed |  | WO Number: | Repaired By: |
| Inspected by (print name): |  | Date: |  |

AMITY REGIONAL SCHOOLS

PREVENTIVE MAINTENANCE – HVAC INSPECTION FORM

| Site Name: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Site Address: |  |  |  |  |
| Building / Wing Number: |  |  |  |  |
| HVAC Unit Make and Model: |  |  |  |  |
| Serial Number: |  |  |  |  |
| Tonnage/Capacity: |  | Date Installed: |  |  |
| Filter Size and Count: |  |  |  |  |
| Inspection Checklist: Condenser Coil Disconnect Condenser Fan Electrical Connections Refrigerant Charge Natural Gas Connection Condensate Drain Ducting/Registers/Grilles Gas Valve/Burner Air Filter Blower Fan Belts (Belt Size: ________________________________ ) Evaporator Coil Lubricate Motors/Shafts Thermostat Pads (evap cooler only) Other (describe): |  |  |  |  |
| Discharge Pressure (5 ton and larger): | Return Air Temp: |  |  |  |
| Suction Pressure (5 ton and larger): | Supply Air Temp: |  |  |  |
| OVERALL CONDITION OF HVAC (check box) Good Fair Poor General Remarks: |  |  |  |  |
| Repairs Needed |  |  | WO Number: | Repaired By: |
| Inspected by (print name): |  |  | Date: |  |

AMITY REGIONAL SCHOOLS

PREVENTIVE MAINTENANCE – CLASSROOM INSPECTION FORM

| Site Name: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Site Address: |  |  |  |  |
| Building / Wing Number: | Room Number: | Class Type (check one) Portable Permanent |  |  |
| Area/Item Inspected: | Condition (check one) | Comments: |  |  |
| Entry Ramps/Handrails | Good Fair Poor |  |  |  |
| Doors and Hardware | Good Fair Poor |  |  |  |
| Floor Covering (carpet) | Good Fair Poor |  |  |  |
| Floor Covering (VCT/lino/rubber/wood) | Good Fair Poor |  |  |  |
| Wall Base | Good Fair Poor |  |  |  |
| Walls and Paint | Good Fair Poor |  |  |  |
| Windows | Good Fair Poor |  |  |  |
| Ceiling | Good Fair Poor |  |  |  |
| Light Fixtures | Good Fair Poor |  |  |  |
| Switches and Covers | Good Fair Poor |  |  |  |
| Outlets and Covers | Good Fair Poor |  |  |  |
| Breaker panel | Good Fair Poor |  |  |  |
| Intercom | Good Fair Poor |  |  |  |
| Sink/Bubbler | Good Fair Poor |  |  |  |
| Cabinets/Countertops | Good Fair Poor |  |  |  |
| HVAC | Good Fair Poor |  |  |  |
| Other (list): | Good Fair Poor |  |  |  |
| OVERALL CONDITION OF CLASSROOM (check box) Good Fair Poor General Remarks: |  |  |  |  |
| Repairs Needed |  |  | WO Number: | Repaired By: |
| Inspected by (print name): |  |  | Date: |  |

AMITY REGIONAL SCHOOLS

PREVENTIVE MAINT. – COMMON AREA/RESTROOM INSPECTION FORM

| Site Name: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Site Address: |  |  |  |  |
| Building / Wing Number: | Inspection Type (check one) Common Area Restroom |  |  |  |
| Area/Item Inspected: | Condition (check one) | Comments: |  |  |
| Entry Ramps/Handrails | Good Fair Poor |  |  |  |
| Doors and Hardware | Good Fair Poor |  |  |  |
| Floor Covering (VCT/lino/ceramic) | Good Fair Poor |  |  |  |
| Wall Base | Good Fair Poor |  |  |  |
| Walls and Paint | Good Fair Poor |  |  |  |
| Windows | Good Fair Poor |  |  |  |
| Ceiling | Good Fair Poor |  |  |  |
| Light Fixtures | Good Fair Poor |  |  |  |
| Switches and Covers | Good Fair Poor |  |  |  |
| Outlets and Covers | Good Fair Poor |  |  |  |
| Breaker Panel | Good Fair Poor |  |  |  |
| Water Closet | Good Fair Poor |  |  |  |
| Urinal/Lavatory | Good Fair Poor |  |  |  |
| Sink | Good Fair Poor |  |  |  |
| Floor Drain | Good Fair Poor |  |  |  |
| Exhaust Fan | Good Fair Poor |  |  |  |
| Other (list): | Good Fair Poor |  |  |  |
| OVERALL CONDITION OF HALLWAY/RESTROOM (check box) Good Fair Poor General Remarks: |  |  |  |  |
| Repairs Needed |  |  | WO Number: | Repaired By: |
| Inspected by (print name): |  |  | Date: |  |